NATIONAL REFINERY LIMITED

7-B, Korangi Industrial Zone, P.O. Box 8228, Karachi-74900 – Pakistan

PABX: +92(21) 35064977-79, 35064981-86.  UAN: +92(21) 111-675-675

Fax +92(21) 35054679, 35054663

TENDER DOCUMENT

FOR

Reverse Osmosis Plants

FY 2025-2026

TENDER REF:  PUR/WHL-8630/2025-2026

DUE DATE: July 17, 2025 AT 3:00 P.M

TERMS & CONDITION

1.	This tender document is issued for inviting bids for Water Treatment Package for RO plants installed at NRL.

2.	Bids are invited as per the terms and condition as contained in the following clauses of this tender document.

3.	In this tender document, wherever the term “NRL” is used will mean “National Refinery Limited” as the buyer – located at 7-B, Korangi Industrial Zone, Korangi, Karachi.

4.	The bid is invited on running rate basis for a contract period of One year from the date of placing of order by NRL.

5.   Pre-Bid Meeting & Sites Visit

A pre-bid meeting and visit of the RO PLANTS  facility for which the water treatment package is required has been scheduled, as given below, to facilitate the bidders to fully understand and ascertain the actual quantum and nature of the job and to seek any clarification before submitting their bids.

Date & Time: July 08, 2025 at 10: 00 A.M

Venue: Room No. 24, Management Block, National Refinery Limited

6.	Due date and time for submission of bid is July 17, 2025 till 2: 30 P.M.

7.     Bids shall be opened on the same day, i.e. July 17, 2025 at 3:00 P.M

8.	Bidding procedure:

Bids are invited on two-envelope system basis, i.e. Technical and commercial bids enclosed in separate envelopes.  The bids shall be opened as under:

8.1	Initially, only Technical Bid envelopes will be opened on the above specified due date & time, i.e. July 17, 2025 at 3:00 P.M. in the presence of NRL bid opening committee.

8.2	The Commercial Bid envelopes shall be retained in custody of NRL without being opened and shall be opened at a later date within the validity period as would be advised by NRL after evaluation and approval of technical offers. The Commercial Bids of only those bidders will be opened in the presence NRL bid opening committee whose technical offers are found responsive/acceptable as per NRL requirement. The commercial bids of those bidders whose offers are technically non-responsive shall be returned un-opened to the respective bidders.

9.	Validity of Bids:

The bids should be valid for 60 days after due date of tender for our consideration. The validity should be extendable by another 30 days, if so required by NRL.

10.	Bid Money:

10.1	Bid Money of Rs. 250,000/- is required to be submitted along with the Technical Bid in the shape of Bank Pay Order favoring National Refinery Limited A/C mentioned company name drawn on a first class scheduled bank of Pakistan. Bank Guarantee/Insurance Guarantee/Cash shall not be acceptable.

10.2	The bid money of those bidders whose bids are technically not responsive/not acceptable shall be returned as soon as the technical bids scrutiny is completed or within two weeks after the validity period of the bids.

10.3	The bid money of successful bidder whom order is placed shall be returned after receipt of Security Deposit / Performance Guarantee as required in clause - 11, below.

11. 	 Security Deposit / Performance Guarantee:

The successful bidder will have to furnish Security   Deposit in the shape of Bank Pay Order in favor of National Refinery Limited, drawn on a first class scheduled bank of Pakistan; OR, a Performance Guarantee (as per format attached as APPENDIX-1) which should be countersigned by a first class scheduled bank of Pakistan for the amount equal to 15% of the order value (net) at the earliest possible but not later than 10 working days from the date of issue of purchase order by NRL.

12.	Supply Order:

12.1		Order(s) for supply of water treatment chemicals (for RO PLANTS) will be placed to single bidder on overall commercially lowest and technical acceptable basis.

12.2	Supply order (PO) shall be placed for the contract period of One year

12.3		The quantity per year of each type of chemicals as per daily dosage/consumption quoted by the bidder in the technical bid shall be considered as the maximum quantity of the respective chemicals required for treatment of water in respective area for the contracted period for placing of order with respective amount as per the price rate quoted.

12.4		The successful bidder will be responsible for dosing/consumption of chemicals to monitor and maintain desired performance of water treatment chemicals (for RO PLANTS) within the parameter of the purchase order & terms / conditions of this tender document. If the consumption of chemicals increases not due to any reported/recorded/agreed problem at NRL end, the supplier will be responsible to supply the additional required quantity of chemicals without any additional cost to NRL.  However, any increase / decrease in the dosing rate of chemicals shall be made with the written consent of NRL.

12.5     The successful bidder is responsible to provide additional chemicals without any additional cost, in case criteria of controlling parameters not match with the initially proposed chemicals in technical offer.

12.6    		In case of any problem at NRL, the supplier will inform NRL in writing by letter within ONE working week of occurring of such problem, which has increased the chemical consumption.  This letter will be evaluated by NRL Technical Services Department and the supplier will be informed regarding acceptance or rejection of their claim.

12.7    The supplier should assign full time monitoring Engineer at site, who will be responsible for preparation of chemicals, laboratory testing of all streams of  RO PLANTS on daily basis and any other Jobs, which will be the required from time to time. The monitoring Engineer will also be responsible for monitoring of all process specification along with chemical consumption, preparation of daily analysis report and available stock of chemicals at warehouse and site (RO PLANTS area). He will also monitor and note down process parameters of RO PLANTS.

13	Supply of Chemicals

13.1   Supply of chemicals will be subject to acceptance by NRL. Chemicals, if any, not accepted or rejected by NRL shall have to be replaced by the bidder within shortest possible time. In case of manufacturer / supplier, the local agent should furnish a certificate attached to their technical bid confirming to replace any un-acceptable/ rejected supply of chemicals as may be intimated by NRL.

13.2   Chemicals which are required on “as & when required basis” shall be supplied as per advice of   NRL Technical Services dept.

13.3   Chemicals with normal requirement shall be supplied on bi-annual basis and with the advice of technical services dept and in view of available quantities in NRL warehouse.

13.4   The vendor shall submit the certificate of analysis / Quality of supplied chemicals for the same manufacturing batch

13.5  HCL is not part of the water treatment package, therefore all bidders should quantify the requirement for their offer package and NRL will directly purchase it from local market. However, cost of these commodity chemicals shall be part of commercial evaluation.

14.	Payment terms:

Payment against supplies will be made within 21 days from the date of receipt of bills along with Delivery Challan in original duly verified/acknowledged by our Warehouse subject to technical acceptance of material by NRL team.  Payment shall be made on actual consumption / requirement basis irrespective of the purchase order / proposed / estimated quantity for defined period.

15.	Price Quotation:

15.1	Price should be quoted in Pak Rupees. Services charges or any other charges will be included in chemical cost.

15.2    The quoted price should be valid for ONE year effective form date of issuance of Purchase order

16.	Submission of Bids:  Bids to be submitted as under:

16.1		Technical Bid should be submitted consisting of two parts as below:

PART A

- Bid Money of Rs. 250,000/- in the shape of Bank Pay Order/Demand Draft favoring National Refinery Limited A/C mentioned company name.

- Information as required shall be submitted by the bidder as per APPENDIX- 2.

PART-B

- TECHNICAL OFFER as per formats attached as SHEETS- 1(A) & 2(A) for offers of water treatment chemicals for RO PLANTS, respectively, mentioning the name of chemicals and quantity offered as required column-wise. Followings should also accompany the Technical Bid:

- Printed literature, if any, showing the specification/properties/application /method of testing of the offered chemicals. All bidders along with technical offer should submit the MSDS of the offered chemicals along with product data/specific sheets.

16.2		Commercial Bid should be submitted as per COMMERCIAL BID Formats, attached with this tender document for price quotation of water treatment chemicals corresponding to chemicals offered   for RO PLANTS, respectively.

16.3		Both Technical and Commercial Bids, complete in all respect and duly signed by authorized person with seal of the bidder, should be sealed in separate envelopes, respectively marked as TECHNICAL BID and COMMERCIAL BID - for Water Treatment Package.  Both these envelopes should then be enclosed in a Master Envelope which should either be personally dropped in the TENDER BOX placed in the NRL reception, at the Refinery’s address before the Due Date & Time. All the envelopes, that is, Technical Bid, Commercial Bid and Master Envelopes should bear Bidder’s Name AND duly marked and addressed as under:

Marked as:		TENDER BOX NO. (LOCAL PURCHASE)

TENDER REF:  PUR/WHL-8630/2025-2026

DUE DATE & TIME: 17-07-2025 (3:00 P. M)

Addressed to:		MANAGER LOCAL PURCHASE

NATIONAL REFINERY LIMITED

7-B, KORANGI INDUSTRIAL ZONE KARACHI (PAKISTAN)

16.4.	Bids sent by mail/courier should reach NRL on due date & Time till 2:30 P.M. However, NRL bears no responsibility for the bids sent by mail. Further bids dispatched through mails / fax will not be entertained.

16.5		Bids received after the Due Date & Time will not be accepted or considered.

17.	Bids Evaluation Criteria:

Bids shall be evaluated as per following criteria:

17.1		Bids with incomplete information or without required enclosures may be rejected/not acceptable.

17.2		Bids without required amount of Bid Money will be rejected.

17.3		Bidder providing evidence of supplying similar chemicals to major oil and gas companies in Pakistan will be given consideration.

17.4		Only offer from internationally renowned and financially sound bidder will be considered.

17.5		Offers of only reputed international brands will be consider.  Locally manufactured/blended chemicals may not be considered.

17.6		Past performance of the bidder will also consider while evaluating the bids.

17.7		The bids offering lowest rate subject to the conditions as laid down in this tender documents.

17.8 	Vendor must submit the software projections that clearly indicate the dosage rate of anti-scalant along with any requirement of acid to maintain the PH of the feed water. The acid will provide by NRL. However, the cost of acid will be added in commercial evaluation. The total package comprised of cost of commodity chemical plus cost of vendors specified chemicals.

18.	Penalty:

Regular supply and performance of the chemicals as per the ordered specification and as required as per this clause (18.1 thru 18. 3) of this tender document is very essential. accordingly, in case of any deviation in the chemicals specification and delivery schedule and/or refusal to supply the chemicals/provide the necessary services for execution of the job on the subject once order is placed shall liable to:

18.1		Cancellation of order and forfeiture/encashment of bidders/supplier’s Bid Money/ Security Deposit/Performance Guarantee, as the case may be.

18.2		De-barring/de-listing of such bidders from doing business/future tendering with NRL.

18.3		Above penalties will also be liable in case of any information/document submitted if found false or incorrect at any time after placing of order.

19.	PERFORMANCE CRITERIA

19.1		Consumption of chemicals as given in Technical/Commercial offers as per Sheets 1(A)/1(B) & A)/2(B) of this tender document.

19.2		Performance of the RO PLANTS system as per operating conditions specified in ANNEX-1 of this tender document.

19.4		To ensure availability of chemicals as defined in clause- 12 & 13 of this tender document.

20.	GENERAL TERMS & CONDITION:

20.1		The supplier shall study the tender documents in detail to assess the quantum of work and type of responsibilities before bidding.

20.2		After awarding the job, the supplier shall strictly follow safety practices and procedures. This includes adequate safety arrangements for his manpower on site.

20.3 	The supplier shall nominate at least one qualified service engineer who shall represent the supplier and conduct all dealings with our Technical service and Utilities Departments. The responsibility of the assigned monitoring Engineer should be as mentioned in Sr.no.11.6

20.4      NRL Technical Services team may conduct interview of the vendor’s services engineer in order to verify the competency, skills and knowledge before assigning in the field.

20.5		Transportation, loading / unloading and manpower arrangement will be the responsibility of the supplier.

20.6		The supplier manpower must be equipped with safety helmet, safety shoes, gloves, safety goggles, PPE’s etc.

20.7		The supplier shall carry out the job carefully so as no damage is done to any NRL equipment/property situated near the work site. The supplier shall be liable for any such damage or loss to NRL.

20.8		Any unsafe practice during execution of job will result in cancellation of the contract at the risk and cost of the supplier.

20.9		In case of delay in supply or sub-standard supply of chemicals, NRL reserve the right to take over the job at any stage from the supplier and get it done through other sources at supplier’s risk and cost.

20.10      NRL reserves the rights to terminate the contract at any time without assigning reason or based on the performance of the chemical programme.

20.11	New RO water treatment programme will start after complete consumption of previous chemicals. New vendor must assign their representative during this Transition period.

20.12     The supplier / vendor  service engineer (field service representative) shall conducted Chemical Cleaning (CIP) of RO plants as per the requirement and as per the direction of NRL Technical Services team.

21.	TECHNICAL SPECIFICTION

NRL is looking for improved Water Treatment Package for RO PLANTS according to Water Management System, which is part of resources management, protecting environment, pollution reduction & ensuring safety.

The program must ensure water & energy conservation with optimization in chemicals consumption to achieve peak efficiency, maintaining the metallurgical integrity and equipment performance. The supplier shall be responsible for all activities including monitoring & advice on chemicals dosage, on-site & off-site testing, suggestions for monetary savings and plant efficiency improvements.

The water treatment package is combination of Anti-scalant / other chemical deemed necessary to meet the KPIs.

On award of contract, the supplier will furnish the following guarantees:

21.1		The supplier will be responsible to maintain the performance of RO PLANTS with respect to supplied chemicals by providing technical back-up services including regular on-site and offsite testing.

21.2		The supplier will ensure and maintain dosing of chemicals as per contract agreement. If the consumption of chemicals is increased vendor will supply additional chemicals without any additional cost to NRL. However any increase/decrease in the dosing rate of chemicals shall be with the consent of NRL.

21.3	The supplier will ensure the dosing of acid to maintain the required PH of feed water. If the consumption of acid is increased then that of specified in the proposal on the same water chemistry. The additional cost of acid is on vendor’s account.

21.4	Performance bond equal to 15% of the contract value will be furnished by the vendor, and will be released after Two years of successful operation, based on the results of two test runs performed at beginning and end of the year.

21.5		Before dosing of all chemical, their physical and chemical properties will be counter checked and certified by NRL laboratory as and when required.

21.6		If any contradiction arises between NRL and Supplier’s laboratory results, then on site testing with the help of Operation and Technical staff of NRL will be carried out to resolve the discrepancy and in case of dispute between NRL laboratory results and Supplier test results third party laboratory testing will be carried out.

21.7		The monitoring schedule will be mutually prepared after selection of vendor.

21.8		All water testing will be carried out as per ASTM / APHA water testing methods.

21.9	Following details are provided as Annexure(s) to this tender document for the selection of suitable water treatment package for NRL to achieve the desired results.

ANNEX-1:	SPECIFICATION/OPERATING CONDITIONS OF

RO PLANTS

ANNEX-2:	WATER CHEMISTRY – FEED WATER FOR

RO PLANTS

22.	Performance Test Run:

Performance test run for water treatment chemicals for RO PLANTS shall be carried out as per operating conditions given in ANNEX-1 and to achieve test results as given in    ANNEX-2.

23	Following formats as APPENDIX & SHEETS are attached with this tender document for submitting the Technical Bid & Commercial Bid as per respective formats.

FOR TECHNICAL BID

APPENDIX-2:	Required information should be provided by the vendor

SHEET-1 (A):	For submitting Technical Bid for Water Treatment Chemicals offered and their consumption for RO PLANTS

[Note: Appendix-2 as Part-A of Technical Bid and Sheets- 1(A) as Part-B of Technical Bid].

FOR COMMERCIAL BID

SHEET-1(B):	For submitting Commercial Bid for the  Chemicals & Quantity as offered in Technical Bid [Sheet-1(A)] for Water Treatment Chemicals for RO PLANTS

24.	Please find below KPI’s of RO PLANTS system

  - Delta P across membranes remains within membranes manufacturer defined limit i.e 30 psi.

  - Minimum numbers of chemical cleanings of RO membranes.

  - No chocking of membranes.

  - No drop in permeate flow rates than that of design.

  - Recovery of RO plants should not less than the design.

  - Permeate quality will remain the same as defined by designer / membrane manufacturer.

  - Acid dosage must remain same as calculated on same PH and Alkalinity values

  - Minimum down town due to chemical cleaning or any other reason related to chemicals.

  - Chemical Treatment Cost should remain as per recommended or agreed values for the whole calendar year.

  - The shipment of all chemicals must be done through country of origin

  - Vendor must share certificate of analysis at the time of delivery at NRL.

  - Date of manufacture and expiry must me mentioned on cans/drums/IBC.

  - Representative or country manager of the successful bidder should meet concerned technical managers of the NRL and he should issue a technical report or minutes of meeting for every fortnightly visit.

  - Representative of the multinational company should submit monthly progress report w.r.t trend of RO PLANTS results.

  - He should also contact foreign expert of their company for problem area of NRL and communicate their guideline to resolve the problems.

  - Vendor must provide competent staff for the cleaning of RO membranes and the team ensure presence during this activity and share pre and post cleaning report.

  - Dosing of the chemical shall be based on the NRL lab results.

  - Vendor is responsible to monitor the performance of multimedia and if require replacement to be taken up and replace in coordination with technical services and utilities. Media to be arranged by contractor as per loading diagram.

  - Vendor is responsible to maintain UF flow rates as per design. Any recommendations that is impacting the flow rates to be taken up and resolve in coordination with technical services and utilities.

  - Vendor is responsible to monitor the performance of cartridge filters. Cartridge filter replacement record to be maintained by contractor.

  - The responsibility for the replacement of cartridge filters lies with the NRL.

  - The flow rate of the UF, RO, and EDI should be properly maintained to prevent any loss of   production.

  - UF outlet SDI should be < 3

  - Vendor is responsible for the performance evaluation of multimedia, UF, RO, and EDI.

  - Vendor will share the lab test results and the entire day's activities via email on regular basis.

  - Vendor is responsible for the excessive chemical dosage and will bear the associated costs.

  - Vendor shall prepare the chemical dosing on a regular basis, early in the morning, in coordination with the operation team.

  - Vendor is responsible for monitoring and calibrating the dosing pumps as required, ensuring the dosage is in accordance with the design specifications.

  - Vendor is responsible to arrange the chemicals for cleaning of RO membranes and its quantity to be adjusted in overall treatment program.

  - Vendor is required to maintained the record of mentioned testing and monitoring daily basis as follows,

- Delta P across Multimedia, UF, cartridge filters and Membranes

- Cartridge filters delta P

- SDI of each plant

- Detail feed chemistry of each RO Plant

- Product feed chemistry of each RO Plant

- Recovery, salt rejection

  - Vendor shall submit Monthly performance report during first week of every month and performance review meeting shall be conducted between vendor, Technical services and Operation utilities representatives.

25.	Each page of the Tender documents shall sign by Authorized representative of the bidder along with stamp in confirmation to contexts of Tender documents.

26.	NRL reserve the right to accept or reject any or all bids without assigning any reason whatsoever.

APPENDIX-1

Guarantee No. 	________________________

Date of Issue 	________________________

Amount		________________________

Date of Expiry	________________________

PERFORMANCE GUARANTEE

Whereas National Refinery Limited, 7-B Korangi Industrial Area, P.O. Box No. 3964, Korangi, Karachi-4 (here in after referred to as the “Buyer”) has accepted the offer against advertised invitation for  “Supply of “Water Treatment Chemicals” vide Tender Ref: PUR/WHL-8630/2025-2026 Due on July 17, 2025 submitted by M/s.______________________________   (here in after referred to as “Seller”) on the Terms and Conditions governing the Tender  Document and subsequent purchase order/letter of offer issued/to be issued by the Buyer.

And whereas the Seller has requested to issue a guarantee for an amount of Rs._______________  (Rupees (in words   __________________________________________).

Now, therefore, in considerations aforesaid, we the ____________________ Bank Limited, hereby undertake the Guarantee of due and satisfactory Performance of the Contract by the Seller in all    respects and we unconditionally and absolutely bind ourselves to the following:

1.	To make payment of Rs. _____________ to the Buyer, or as directed by the Buyer, on the date of   the receipt of demand from the Buyer in writing without reference to the Seller, and without any question whatsoever.

2.	To keep this Guarantee valid and in force for the period upto ___________________ from the effective date of purchase order/letter of offer plus one month after completion of supply of the total quantity of goods.

3.	To extend the Guarantee for such further period as may be required by the Buyer in Buyer’s sole discretion five days before the expiry of the validity date.

Our this Guarantee is unconditional, and the sole judge for deciding whether the Seller has supplied the goods as per Purchase Order afore-mentioned and fulfilled the Terms & Conditions of the Order, will be the Buyer.

Any grant of time or indulgence to the seller without reference to us shall not in any manner absolve us from our liability to make payment to the buyer as stipulated above under this Guarantee.

Our commitment under this Guarantee is limited in amount of Rs. ____________________.

For: Full Name of Guarantor (Bank) (A First Class Scheduled Bank of Pakistan) Branch/Office Address, Phone & Fax

Signature								Signature

Designation							Designation

NOTE: Do not form part of the Guarantee 1. Stamp paper to be issued in the name of Guarantor. 2. Stamp paper issue date should be of or before the date of issue of Guarantee. 3. Contents of stamp of vendor should be legible. 4. Date of Expiry of Guarantee should be determined by NRL. 5. Prior approval from relevant department of NRL to be taken in selection of Name of the Guarantor.

APPENDIX-2

# INFORMATION REQUIRED FROM THE VENDORS

TECHNICAL BID (PART-A)

Required information should provide by vendor:

1.	Local Company/Agent:  Registered Name, Address, Tele phone and Fax Numbers, E-Mail, etc. and Company profile.

2.	Foreign Principal: Name, Address, Telephone & Fax Numbers, Mailing Address, E-Mail, etc. and Company profile.

3.	Detail of experience, including reference list of end-users/refineries inside and outside Pakistan and their performance certificate.

4.	Detail of local technical back-up services, such as resource manpower, their status, qualification and experience of technical staff regarding monitoring and testing of similar water treatment systems.

5.	Status/details of laboratory setup in Karachi and list of laboratory and portable equipments for water testing.  NRL team of engineers will visit the local laboratory facilities.

6.	Letter of Authorization (hard copy in original) from manufacturer/principal in favor of local agent/supplier.

7.	Letter of Authorization from the Principal that the local agent has the required capability in terms of equipment and human resource for monitoring of the water system.

8.	Details of financial health of the principal and local company with a copy of bank statement, audited accounts of last 12 months.

9.	National Tax number, status and registration date.

10.	No litigation certificate by the company.

11.	Any other information, which may be considered by the company to entitle them for pre-qualification.

12. Vendor will be responsible to monitor and ensure preparation of the chemicals on daily basis in coordination with technical services and operations. CPR prepare technical reports of RO PLANTS  on daily basis and submit the report to concern dep’t, He will also assigned full time technical person at NRL site for close monitoring and performance of their chemicals.

13.	All vendors must submit concentration of polymers along with offered chemicals from their foreign principal and successful bidder should also mention it in the each shipment of their chemicals to NRL.

NOTE:		1)	Bids received with incomplete information will not be considered.

2)	Any information/document submitted if found incorrect/false at any time will result in cancellation of order if placed on the party.

ANNEX-1

SPECIFICATION / DESIGN CONDITIONS OF RO PLANTS

| S.No | Design Parameters | RO 1 | RO2 | RO3 | RO4 | RO-5 | RO-EDI-1 | RO-EDI-2 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Permeate production (IGPD) | 100,000 | 200,000 | 300,000 | 250,000 | 350,000 | 400,000 | 400,000 |
| 2 | Recovery (%) | 50 | 60 | 75 | 50 | 50 | 90 | 90 |
| 3 | Feed water | Brackish water | Brackish water | Brackish water + RO-1,2 Reject | well water + RO-1,2,3 Reject | Well water +RO-4 Reject | Permeate of All RO’s |  |
| 4 | Feed water TDS | 10,000 | 10,000 | 10,000 | 10,000 | 18,000 | 700 |  |
| 5 | Product TDS ppm | < 100 | < 150 | < 250 | < 250 | <275 | 10-15 |  |
| 6 | Stage | Single stage | Two stage | Two stage | Single stage | Single stage |  |  |
| 7 | Membranes | Brackish water | Brackish water | Brackish water | Sea water | Sea water | Brackish water |  |
| 8 | Membranes company | Dow Film tech | Dow Film tech | Dow Film tech | Dow Film tech | Hydranautics | Dow Film tech |  |
| 9 | UF | NA | NA | Available | Available | Available | NA |  |
| 10 | MMF | Available | Available | Available | Available | Available | NA |  |
| 11 | Charcoal Filter | NA | NA | Not in use | Not in use | Available | NA |  |
| 12 | No. of Membranes | 25 | 48 | 91 | 84 | 84 | 72+72 =144 |  |

Note:

Recovery is subject to the feed water chemistry. It may increase if we operate at lean feed and vice versa.

ANNEX-2

WATER CHEMISTRY FOR RO PLANTS

| RO's FEED WATER CHEMISTRY |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Parameters | RO-1 | RO-2 | RO-3 | RO-4 | RO-5 | RO-EDI-1 | RO-EDI-2 |
| PH | 8.2 | 8.2 | 8.4 | 8.4 | 8.4 | 7.2 | 7.2 |
| TDS (ppm) | 5500 | 5500 | 8000 | 10,000 | 16,000 | 700 | 700 |
| Calcium as ppm of CaCO3 | 400 | 400 | 650 | 850 | 1450 | 50 | 50 |
| Magnesium as ppm of CaCO3 | 650 | 650 | 770 | 900 | 1700 | 25 | 25 |
| Total Hardness as ppm of CaCO3 | 1050 | 1050 | 1320 | 1650 | 3150 | 75 | 75 |
| Sulphate as ppm of CaCO3 | 450 | 450 | 750 | 1050 | 2550 | 10 | 10 |
| Sulphides ppm | 2 | 2 | 3 | 4 | 5 | 8 | 8 |
| Free Chlorine , ppm | Nil | Nil | Nil | Nil | Nil | Nil | Nil |
| Ortho Phosphate, ppm | 0.2 | 0.2 | 0.3 | 0.3 | 0.3 | Nil | Nil |
| Chloride, ppm | 1500 | 1500 | 2200 | 3000 | 4000 | 200 | 200 |
| TSS, ppm | 5 | 5 | 5 | 5 | <5 | <5 | <5 |
| Oil contents, ppm | Nil | Nil | Nil | Nil | Nil | Nil | Nil |
| Total Iron, ppm | 0.1 | 0.1 | 0.2 | 0.2 | 0.3 | 0.1 | 0.1 |
| Sodium, ppm | 966 | 966 | 1500 | 1770 | 3000 | 275 | 275 |
| Potassium, ppm | - | - | - | - | - | 10 | 10 |
| Barium, ppm | - | - | - | - | - | - | - |
| Strontium, ppm | - | - | - | - | - | - | - |
| Aluminum, ppm | - | - | - | - | - | - | - |
| Manganese, ppm | - | - | - | - | - | - | - |
| Fluoride, ppm | - | - | - | - | - | - | - |
| CO2 , ppm | 7.04 | 10.56 | 28.16 | 30.32 | 30.32 | 50 | 50 |
| Nitrate, ppm | - | - | - | - | - | 5 | 5 |
| Carbonates, ppm | 500 | 500 | 700 | 800 | 1000 | 0 | 0 |
| Bicarbonate, ppm | 1000 | 1000 | 1500 | 1700 | 2200 | 65 | 65 |

Note:

- Balance the ions if required for projections purpose.

- Acid dosing facility is not available at RO-1 &2 and RO-EDI-1 & 2

- Aid dosing facility is available at RO-3,4 and 5

- After Acid dosing PH of RO-5 would be around 7.9 (Correct feed water PH up to 7.9 and calculate acid and anti scalant dosing)

- After Acid dosing PH of RO-3 & 4 would be around 7.9 (Correct feed water PH up to 7.9 and calculate acid and anti scalant dosing)

WATER TREATMENT CHEMICAL CONSUMPTION FOR RO PLANTS

TECHNICAL BID (SHEET-1A)

365 days /year

| Sr. # | Chemical Name | Function | Initial dosage (Kg) |  |  |  |  |  |  |  |  |  | Regular Chemical Consumption (kg/day) |  |  |  |  |  |  |  | Total Consumption |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | RO-1 | RO-2 | RO-3 | RO-4 | RO-5 | RO-EDI-1 | RO-EDI-2 | Total | Period (days) | Total | RO-1 | RO-2 | RO-3 | RO-4 | RO-5 | RO-EDI-1 | RO-EDI-2 | Total | Total / year | Kg / year |
|  |  |  | A | B | C | D | E | F | G | H | I | J (H x I) | K | L | M | N | O | P | Q | R | R X 365 | R + J |
| 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 4 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

* 1)	Quantity & duration of Initial dosage and dosage during switching from old system to completely new system, i.e. transition phase consumption of chemicals should be carefully calculated.

NAME & ADDRESS OF BIDDER:  ________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

PHONE: ______________________    FAX: _____________________

SIGNATURE & SEAL OF BIDDER: _________________________________________________________

WATER TREATMENT CHEMICAL CONSUMPTION FOR RO PLANTS

# COMMERCIAL BID (SHEET 1B)

# 365 days/year

| Sr. # | Chemical Name | Total Initial Dosage Quantity to be specified by bidder as quoted in Technical Bid | Total Regular Consumption for One Year Quantity to be specified by bidder as quoted in Technical Bid | Combined Total Consumption for One Year [Initial + Regular] | #### PRICE (Per Kg) | ## AMOUNT ## [For combined total ## Qty. for One year] |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | A | C | D = A+B+C | #### E | ## F = D*E |
|  |  | Kg | Kg /Year | Kg | #### PKR /Kg | ## PKR |
| 1 |  |  |  |  |  |  |
| 2 |  |  |  |  |  |  |
| 3 |  |  |  |  |  |  |
| 4 |  |  |  |  |  |  |

TOTAL COST IN PKR:                              .

Name & address of bodder:_________________________________________________________________________________

Phone :_________________________ Fax:_____________________________ email:__________________________________